Hub BP Jeweller

Wireless control panel with the external battery as a power source. Supports photo verification. Connectable via two SIM cards (2G/3G/LTE)

| # Capacity | Ajax devices up to 100 Specifically, up to 10 sirens or keypads with a built-in siren and up to 5 range extenders. Ajax NVRs up to 36 Ajax cameras up to 224 via Ajax NVRs and up to 492 standalone Third-party IP cameras up to 10 when using RTSP via SDK up to 224 when using ONVIF via Ajax NVRs Users up to 50 - Any number of admin users within the hub limit. - PRO accounts for installers. - PRO accounts for installation and monitoring companies. - Access management for users. Automation scenarios up to 32 - By alarm. - By schedule. - By arming/disarming. - By temperature, humidity, CO2 concentration. - By pressing Button. - By touching LightSwitch. Security groups up to 9 Rooms up to 50 Event log up to 1,000 events Events are saved on the non-volatile onboard flash memory. |
| --- | --- |
| # Wireless communication | Jeweller communication technology Proprietary wireless communication technology to transmit commands, alarms, and events. Key features: - Two-way communication. - Advanced anti-sabotage. - Block encryption featuring a dynamic key. - Instant notifications. - Remote control and configuration in Ajax apps. Frequency bands 866.0–866.5 MHz 868.0–868.6 MHz 868.7–869.2 MHz 905.0–926.5 MHz 915.85–926.5 MHz 921.0–922.0 MHz Depends on the sales region. Maximum effective radiated power (ERP) up to 25 mW Automatic power control to reduce power consumption and radio interference. Radio signal modulation GFSK Radio communication range up to 2,000 m up to 6,500 ft Between a hub and connected devices (in an open space). The maximum range depends on the connected device. Polling interval from 12 s to 300 s Adjusted by a PRO or user with admin rights in Ajax apps. Encrypted communication All stored and transmitted data are protected by block encryption featuring a dynamic key. Frequency hopping To prevent radio interference and jamming. Wings communication technology Proprietary wireless communication technology to transmit photos. Key features: - Two-way communication. - Advanced anti-sabotage. - Block encryption featuring a dynamic key. - Data packages reload in case of transmission errors. - Photo delivery check. Frequency bands 866.0–866.5 MHz 868.0–868.6 MHz 868.7–869.2 MHz 905.0–926.5 MHz 915.85–926.5 MHz 921.0–922.0 MHz Depends on the sales region. Maximum effective radiated power (ERP) up to 25 mW Automatic power control to reduce power consumption and radio interference. Radio communication range up to 2,000 m up to 6,500 ft Between a hub and connected devices (in an open space). The maximum range depends on the connected device. Encrypted communication All stored and transmitted data are protected by block encryption featuring a dynamic key. Frequency hopping To prevent radio interference and jamming. |
| # Recommendations | Hub BP Jeweller is designed for indoor use only. |
| # Communication channels | Cellular 2 × micro SIM slot Cellular bands 2G GSM900/DCS1800 (B3/B8) 3G WCDMA 850/900/2100 (B1/B5/B8) 4G (LTE) FDD B1/B3/B5/B7/B8/B20 Automatic switching between communication channels between SIM cards — up to 4 minutes Communication channels prioritization 1. Micro SIM slot 1 2. Micro SIM slot 2 Auto APN The APN auto select feature allows setting access point automatically based on the installed SIM card. External antenna connectors Jeweller Wings 4G (LTE) The system will notify of the damaged antenna. Ajax ExternalAntenna is sold separately. Alarm transmission system categories SP5 Control panel operation method pass-through Signaling security S2 Substitution security. Information security I2 |
| # Notifications | Notification types - Push notifications - SMS - Calls Event types - Alarms - Malfunctions - Security state change - System events - Non-security alerts - Automation devices Notification types are configured individually for each user. Notifications can be customized for A–D schemes according to EN 50131 requirements. |
| # Photo verification | Photo verification types - Photo by alarm - Photo by scenario - Photo on demand - Photo by schedule The Photo by Schedule feature is available for hubs with OS Malevich 2.19 firmware version or later. Photo delivery time up to 9 s By default. Photo resolution up to 640 × 480 pixels Depends on the detector. Number of photos in a series from 1 to 5 pictures |
| # Monitoring | Supported protocols - SIA DC-09 (SIA-DCS) - SurGard (Contact ID) - ​​ADEMCO 685 - Other proprietary protocols Event types - System alarms and events - Panic button coordinates - Photo verification |
| # Power supply | External 4.2–16 V⎓, up to 2 A Zinc-air battery or external power source. Internal 4.2–16 V⎓, up to 2 A Rechargeable lead-acid and LiFePO4 batteries (not included). Non-rechargeable LTC batteries (not included). Device operating DC voltage range 3.5–16 V⎓ |
| # Autonomous operation | On external battery in full function mode up to 18 months On a 12 V⎓, 600 Ah, zinc-air non-rechargeable external battery (not included). On external battery in Battery saving mode more than 5 years On a 12 V⎓, 600 Ah, zinc-air non-rechargeable external battery (not included). On internal battery in a Battery saving mode up to 17 months On a 7.2 V⎓, 95 Ah, LTC non-rechargeable Internal battery NB (7.2V/95Ah) (not included). up to 4 months On a 6.4 V⎓, 27 Ah, LiFePO4 rechargeable Internal battery RB (6.4V/27Ah) (not included). up to 2 months On a 12 V⎓, 7 Ah, lead-acid rechargeable internal battery (not included). |
| # Sabotage protection | Tamper alarm Notifications on attempts to detach the device from the surface or remove it from the mounting panel. Protection against spoofing device authentication Frequency hopping The hub sends notifications to all users and the security company of jamming or losing connection with the devices. Jamming alert Hub BP Jeweller analyzes the channel’s noise level and the quality of communication with added devices and sends an alert in 30 seconds. |
| # Enclosure | Dimensions 196 × 238 × 100 mm 7.72″ × 9.37″ × 3.94″ Weight 1,010 g 35.63 oz Operating temperature range from −10 °C to +40 °C from 14 °F to 104 °F Operating humidity up to 75% Protection class IP40 |
| # Colors | Black White |
| # Complete set | Hub BP Jeweller Casing Installation kit Quick start guide |
| Warranty | 24 months |